| Y | N | Items to check for: Fire Code references: |
| --- | --- | --- |
| GENERAL BUILDING ITEMS |
|  |  | Building’s address shall be clearly legible and visible from the street FC 901.4.4 |
|  |  | Approved Certificate of Occupancy / Certificate of Compliance posted FC 103.2.1.1 |
|  |  | Where present: Fire Department Connections maintained, properly identified and unobstructed FC 1001.5.1 & FC 1001.7 |
|  |  | Building 100% sprinkled; Partial : Main Lobby / Exit discharge floor Common areas Basement Atrium |
|  |  | Fire Alarm permit current (per COH False Alarm Ordinance) |
|  |  | Audibility of Fire Alarm system adequate (15 Decibels or more over ambient sound levels) throughout all areas of building FC 1007.3.3.3.3 |
|  |  | Audibility of Fire Alarm system verified and documented at least every three years FC 1007.3.3.3.3 |
|  |  | Fire Department required permits current (see list below) FC 105.8 |
|  |  | All exterior exit doors have approved locking devices FC 1207.3 |
|  |  | All exterior exit doors have an adequate discharge landing |
|  |  | All exterior exit discharge pathways have adequate lighting to the public way FC 1211.1 |
|  |  | All storage area and maintenance spaces shall be orderly FC 1103.3.2.1 |
|  |  | Use of combustible decorative materials in accordance with Fire Code FC 1103.3.3 |
|  |  | No fueled equipment stored in building, except in rooms approved for such FC 1103.3.2.6 |
|  |  | Approved Fire Lanes provided and maintained FC 902 |
| ROOF / PENTHOUSE LEVEL |
|  |  | Standpipe manifold valve(s) at roof level or upper standpipe terminus |
|  |  | Standpipe pressure gauge at roof manifold or upper standpipe terminus FC 1001.5.1 |
|  |  | All standpipe pressure gauges have double drain assembly FC 1001.5.1 |
|  |  | Building lightning rod ground wire connected to standpipe components FC 8504 |
|  |  | Gravity tank(s) provided for standpipe water supply |
|  |  | Wooden cooling tower structure(s) present |
|  |  | Wooden cooling tower structure protected by Sprinklers or Fire Hoses |
|  |  | Building emergency generator located on open roof |
|  |  | Building emergency generator located in a penthouse |
|  |  | Where present: Emergency generator in 2-hr occupancy separation (after 9/21/81) |
|  |  | Approved fuel tank and/or fuel storage containers for emergency generator FC 7902 |
| Type of fuel for generator: | Diesel | Natural Gas |
|  |  | Approved fire department access to roof |
|  |  | Elevator penthouse / air handler equipment room on roof |
|  |  | Metal or metal-lined containers with lids for oily rags in elevator room FC 1103.2.1.3 |
|  |  | Fire extinguishers and fire hoses in penthouse, properly mounted, identified and current service tags affixed FC 1002.1 |
|  |  | Fire hoses pressure tested every 3 years FC 1001.5.2 |
|  |  | Roof access through penthouse or mechanical room |
|  |  | Exit signs provided and properly maintained (including emergency bulb for exit lights) FC 1212.4 |
|  |  | No exposed electrical wiring, missing electrical equipment covers/parts, etc. FC 8504 |
| Electrical panels: | No open slots – missing inserts or parts: FC 8504 | No missing, faded panel index cards or directories, inadequate labeling: FC 8509.3 |
|  |  | Stairwell pressurization / smoke removal equipment present |
|  |  | Stairwell pressurization tested every 5 years FC 1001.5 |
|  |  | Air handler, electrical or mechanical rooms free of combustible storage FC 1103.3.2.4 |
|  |  | All Floor penetrations properly sealed with approved 2-hr fire stop materials FC 1112.1 |
| EXIT STAIRWAYS |
|  |  | Water pressure gauges, with double drain assembly, installed at standpipe upper terminus FC 1001.5.1 |
|  |  | 2-hour fire rating maintained throughout enclosed exit stairway system FC 1210.1 |
|  |  | Emergency Lighting provided; Type: Generator Battery Units only FC 1211.2 |
|  |  | Stairways free of any storage or obstructions FC 1203 & FC 1210.3 |
|  |  | Electronic egress control devices on exit / stairway doors; Permitted/approved/tags affixed by City Building Department FC 1207.5 |
|  |  | Approved stair identification, terminus & roof access signs provided within stairway FC 1212.4.1 |
|  |  | Approved reentry or reentry means provided on all locked designated reentry floors FC 1210.7 |
|  |  | Approved stair identification and reentry signs provided on occupancy side of stairway doors FC 1210.4.2 |
|  |  | Exit stairways discharge to the exterior; Discharge back into building |
|  |  | Approved exit door devices on exit discharge level doors FC 1207.3 |
|  |  | Approved area of discharge; provided with emergency lighting throughout FC 1211.2 |
|  |  | Standpipe hose valve thread protective caps in place and tight FC 1001.5.1 |
|  |  | Pressure reducing valves or devices provided on stairway standpipe outlets |
|  |  | Pressure reducing valves tested within last 5 years FC 1001.5.1 |
| EXIT CORRIDORS |
|  |  | 1-HR rated exit corridor fire rating maintained on all floors FC 1209 |
|  |  | 2-HR rated exit corridor fire rating maintained on Sky-Lobby floors FC 1209 |
|  |  | Exit signs provided and properly maintained (including emergency bulb for exit lights) FC 1212.4 |
|  |  | Corridors free of storage and / or obstruction FC 1203 |
|  |  | Fire extinguishers and fire hoses in penthouse, properly mounted, identified and current service tags affixed FC 1002.1 |
|  |  | Fire hose pressure tested every 3 years FC 1001.5.2 |
|  |  | Approved elevator lobby evacuation signs and graphics provided FC 1213.2 |
|  |  | Electronic locks on corridor doors | Permitted & Approved FC 1207.5 |
|  |  | Electronic locks in elevator lobbies | Permitted & Approved FC 1207.5 |
|  |  | Approved emergency Exitway lighting provided FC 1211.2 |
|  |  | Approved emergency lighting: Type: Generator Battery units only FC 1211.2 |
|  |  | Janitorial closets/rooms - approved storage heights maintained FC 1103.3.3.2 |
|  |  | All Electrical and Mechanical rooms properly identified FC 8509 |
|  |  | Electrical & mechanical rooms free of combustible storage FC 1103.3.2.4 |
|  |  | Electrical panels unobstructed, 30 inch clearance work space FC 8509.2 |
|  |  | All electrical control boxes, throw switch boxes, breaker switch panels adequately identified and labeled FC 8509.3 |
|  |  | Approved light guards / bulb protectors in place where required FC 8504.2 |
| GUEST FLOORS / APARTMENTS |
|  |  | Fire Alarm Pull Stations readily visible and unobstructed FC 1001.7.4 |
|  |  | Fire hoses / fire extinguisher cabinets readily visible and unobstructed FC 1001.7 |
|  |  | Fire hoses / fire extinguishers affixed with current annual inspection/service tags FC 1001.5.2 & FC 1002.1 |
|  |  | Fire hoses pressure tested every 3 years FC 1001.5.2 |
|  |  | Adequate, approved exiting provided and maintained: no exiting through storerooms, kitchens, mechanical rooms, or other hazardous areas FC 1213.3 |
|  |  | Approved guest sleeping unit / apartment door locking devices provided FC 1207.3 |
|  |  | Automatic door closing devices provided on guest sleeping unit / apartment corridor doors FC1209 |
|  |  | Approved exit corridor door locking devices provided FC 1207.3 |
|  |  | Electronic egress control devices provided (magnetic locking devices): Permitted and approved FC 1207.5 |
|  |  | Exit signs maintained in proper working conditions (including emergency bulb for exit lights) FC 1212.4 |
|  |  | Adequate exitway directional signs provided and properly positioned FC 1212.2 |
|  |  | Exit doors adequately identified and distinguishable from other doors FC 1207.6 |
|  |  | Exit pathways free from storage and obstruction FC 1203 |
|  |  | Janitorial/storage closets/rooms approved storage heights maintained FC 1103.3.2.2 |
|  |  | Storage heights maintained in guest/tenant storage rooms/spaces FC 1103.3.2.2 |
|  |  | All electrical and mechanical room doors properly identified FC 8509 |
|  |  | All electrical and mechanical room doors kept locked or provided with automatic door closers FC 1209 |
|  |  | All electrical and mechanical closets/ rooms free of combustible storage FC 1103.3.2.4 |
|  |  | Electrical panels and equipment unobstructed FC 8509.2 |
|  |  | Electrical wall outlet and switch cover plates in place as required FC 8504 |
|  |  | Electrical extension cords used in an approved manner FC 8506.1 |
|  |  | Power taps (strips) used in an approved manner FC 8508 |
|  |  | All guest use clothes dryers are properly vented FC 1107 |
|  |  | Laundry equipment, spaces around/behind equipment free of dust/lint accumulation FC 1107 |
|  |  | Ceiling tiles in place, in all areas where installed or required to help prevent fire/ smoke extension and increase efficiency of smoke detection and fire suppression systems FC 1113 |
|  |  | Approved trash & waste storage provided FC 1103 |
|  |  | Dumpster permit required; Permit current FC 105.8.c |
|  |  | Open flame cooking devices (barbecue pits, grills, woks, etc.) used on building balconies FC 1102.5.2.2 |
| PUBLIC ASSEMBLY / KITCHEN AREAS |
|  |  | Exit and directional signs provided as required and properly maintained (including emergency bulb for exit lights) FC 1212.4 |
|  |  | Fire hoses / fire extinguishers affixed with current annual inspection/service tags FC 1001.5.2 & FC 1002.1 |
|  |  | Fire hoses pressure tested every 3 years FC 1001.5.2 |
|  |  | Certificate of Occupancy / Certificate of Compliance posted FC 103.2.1.1 |
|  |  | Approved door locking devices used in assembly areas FC 1207.4 |
|  |  | Public Assembly permit posted FC 2501.3 |
|  |  | Assembly occupancy capacity posted FC 2501.16 |
|  |  | Proper use of extension cords and power taps observed in assembly areas FC 8506 & FC 8508 |
|  |  | Service corridors exit passageways unobstructed FC 1203 |
|  |  | Gas pressure / leak test current (every last 5 years) FC 1106 |
|  |  | Kitchen provided with approved vent hood system (wherever grease laden vapors are produced) FC 1006.1 |
|  |  | Commercial Kitchen vent hood provided with approved automatic fire suppression system FC 1006.2 |
|  |  | Vent hood fire suppression system inspected / tagged every 6 months FC 1006.2.8 |
|  |  | Cooking surfaces, floors, walls and hood systems free of grease and oil accumulations FC 1006.2.8 |
|  |  | Approved listed portable fire extinguishers provided for kitchen and dining areas FC 1006.2.7 |
|  |  | Apartments only: Listed 2-A,10B:C portable fire extinguisher provided for each unit FC 1002.1, HFD STD 10-2 |
|  |  | Approved storage height clearance maintained in all kitchen and storage areas: ( Sprinklers - 18 inches; No sprinklers - 24 inches ) FC 1103.3.2.2 |
|  |  | No electrical shock hazards present in freezer / chiller rooms / scullery/ food prep areas (exposed wiring or light bulbs) FC 8504 |
|  |  | No exposed electrical wiring, missing electrical equipment covers/parts, etc. FC 8504 |
|  |  | All electrical breaker panels and control switches unobstructed FC 8509.2 |
|  |  | Proper use of extension cords and power taps observed FC 8506 & FC 8508 |
|  |  | Approved exiting maintained in kitchen and dining areas FC 1204.2.1 |
|  |  | LP Gas used in building; Use / storage in accordance with Code requirements FC 8201 |
|  |  | Candles/Open flames devices used in building; Use is in accordance with Fire Code FC 1109.8 |
|  |  | Use of combustible decorative materials in accordance with Fire Code FC 1103.3.3 |
| MAIN LOBBY / EXIT DISCHARGE LEVEL |
|  |  | Main building exit doors have proper signs provided, as needed FC 1207.3 |
|  |  | All electronic exit egress control devices permitted and approved FC 1207.5 |
|  |  | Areas of exit discharge adequate and safely maintained FC 1213.1 |
|  |  | Approved Fire Command Center provided (high-rises buildings only) FC 1113 |
|  |  | Fire Depository Box provided & maintained (high-rises buildings only) FC 902.5 |
|  |  | 9-1-1 Lock / Key Box provided& maintained, where required |
|  |  | Fire Alarm system in proper working order and inspection tagged FC 1001.5.3 & FC 1007 |
|  |  | Elevator(s) in good operating condition |
|  |  | Elevator keys available | All keys function properly |
|  |  | Elevator Fire Service Phase I Recall provided & in working order FC 1001.5.3 |
|  |  | Elevator Fire Service Phase II provided & in working order FC 1001.5.3 |
|  |  | Elevator(s) monthly testing documented as required by Elevator Code |
| BASEMENT / BELOW GRADE / WINDOWLESS LEVELS |
|  |  | Stairway barriers in place between exit discharge level and basement FC 1210.2 |
|  |  | Basement fully sprinkled; Partial No Sprinklers FC 1001.5.1 |
|  |  | Adequate unobstructed exiting provided throughout FC 1203 |
|  |  | Adequate Exit and Exit Directional signs provided and maintained (including emergency bulb for exit lights) FC 1212.4 |
|  |  | Approved emergency exit lighting provided; type: Generator Battery units FC 1211.2 |
|  |  | All combustible storage kept at approved heights and aisle widths FC 1103.3.2.2 |
|  |  | Light guards / tube protectors provided as required FC 8504.2 |
|  |  | Fire hoses and fire extinguishers provided, identified, unobstructed and service tags affixed FC 1001.5.1 |
|  |  | Fire hose pressure tested every 3 years FC 1001.5.2 |
|  |  | No Class I flammable liquids in use or being stored in basement FC 7902.5.10.1 |
|  |  | Flammable / combustible liquids stored in approved rooms / cabinets FC 7902 Permit required FC 7901.3 ; Permit current FC 105.8f |
|  |  | Trash and waste stored in approved location FC 1103 |
|  |  | All electrical panels labeled and have directories FC 8509.3 |
|  |  | No exposed electrical wiring, missing electrical equipment covers/parts, etc. FC 8504 |
|  |  | All electrical control panels and switches accessible / unobstructed FC 8509.2 |
| SERVICE AREAS / CENTRAL PLANT / MAINTENANCE FACILITIES |
|  |  | Laundry equipment properly vented FC 1107 |
|  |  | Laundry equipment and areas free of dust/lint accumulation FC 1107 |
|  |  | Central Plant area fully sprinkled; Partial sprinklers; No Sprinklers FC 1001.5.1 |
|  |  | Adequate Exit and exit directional signs provided FC 1212.1 |
|  |  | Fire hose / fire extinguishers affixed with current annual inspection/service tags FC 1001.5.2 & FC 1002.1 |
|  |  | Fire hose pressure tested every 3 years FC 1001.5.2 |
|  |  | Standpipe system(s) risers and valves adequately identified FC 1001.5.1 |
|  |  | Standpipe system(s) risers and valves inspected and service tags affixed FC 1001.5.1 |
|  |  | Sprinkler system(s) risers and valves adequately identified FC 1001.5.1 |
|  |  | Sprinkler system(s) risers and valves inspected and service tag affixed FC 1001.5.1 |
|  |  | Fire pump(s) and water supply tank(s) inspected and service tag affixed FC 1001.5.1 |
|  |  | Approved fuel tank and/or fuel storage containers for fuel-driven fire pump FC 7902 |
|  |  | Any special fire suppression systems properly maintained and tagged FC 1001.5.1 |
|  |  | Fire alarm system(s) fully operational and service tag affixed FC 1001.5.1 |
|  |  | Boiler Permits for State/City current |
|  |  | Annual Elevator inspections current |
|  |  | Flammable / combustible liquids stored in approved rooms / cabinets FC 7902 Permit required FC 7901.3; Permit current FC 105.8f |
|  |  | Hazardous chemical properly identified and stored; FC 8001. Permit required FC 8001.3; Permit current FC 105.8h |
|  |  | MSDS provided for hazardous materials used /stored on premises FC 8001.6 |
|  |  | HMIS provided for permitted hazardous materials used /stored on premises FC 8001.3.3 |
|  |  | All compressed gas cylinders properly stored FC 7401.6.4 |
|  |  | Service, maintenance and storage areas maintained clean and orderly, free of excess combustible waste accumulation and clutter FC 1103 |
|  |  | Electrical panel and switch adequate labeled; FC 8509.3 Panel unobstructed FC 8509; No missing or exposed parts or wiring FC 8504 |
|  |  | No exposed electrical wiring, missing electrical equipment covers/parts, etc. FC 8504 |
|  |  | Where present: Emergency generator in 2-hr occupancy separation (after 9/21/81) |
|  |  | Approved fuel tank and/or fuel storage containers for emergency generator(s) FC 7902 |
|  |  | Emergency generator passed annual load testing requirements FC 1001.5.2 |
|  |  | Fire Doors/Fire Dampers inspected in accordance with FC requirements FC 1001.5.2 |
| PARKING FACILITIES |
|  |  | All emergency exit signs readily visible & properly maintained FC 1212.4 |
|  |  | Fire hoses provided and identified, current service tags affixed FC 1001.5.1 |
|  |  | Fire hose pressure tested every 3 years FC 1001.5.2 |
|  |  | Adequate Fire extinguishers provided and identified, current tags affixed FC 1002.1 |
|  |  | Parking facility 100% sprinklered; Partial sprinklers, No sprinklers FC 1001.5.1 |
|  |  | Emergency exit lighting in proper order, where required FC 1211.2 |
|  |  | Where present: Standpipe system inspected and tagged FC 1001.5.1 |
|  |  | Where present: Standpipe upper terminus provided with approved pressure gauge(s), with double drain valve assembly FC 1001.5.1 |
|  |  | All flammable / combustible liquids stored in approved rooms / cabinets FC7902 Permit required FC 7901.3 ; Permit current FC 105.8f |
| Houston Fire Department Permits |
| * Where required, the following permits require annual renewal: |
|  |  | Combustible Waste Storage (over 50 cu. ft. - dumpster) FC 105.8c |
|  |  | Compressed gases (to use, store, handle, dispense) FC 105.8c |
|  |  | Fire Alarm System permitted (per COH False Alarm Ordinance) |
|  |  | Flammable & Combustible Liquids (to use, store, handle, dispense) FC 105.8f |
|  |  | Hazardous Materials (to use, store, handle, dispense) FC 105.8h |
|  |  | Key Boxes or Fire Depository Boxes FC 105.8k |
|  |  | Public Assembly (over 50 persons) FC 105.8p |

This guide is not intended to be complete and totally comprehensive. Its intent is as a quick reference for the most commonly noted items to be aware of or observed during general hotel / motel occupancy inspections. High-rise hotel / motel occupancies shall meet such additional requirements as may be required of all high-rise occupancies.

All Fire Code references are from the City of Houston Fire Code (Uniform Fire Code, 1997 Edition, As Amended).

* Questions regarding permit fees should be directed to: Houston Fire Department Permit Office, 1205 Dart Street {off of Houston Avenue}, Houston, TX 77007; During normal business hours telephone: (713) 247-8557.